## Sheet1
details of clauses required to test/check
SN | CLAUSE NO. | DESCRIPTION | TEST REQUIRED | CERTIFICATION REQUIRED | UNDERTAKING/DECLARATION | DATA SHEET | TO BE CONFIRMED
| 2.1 (G) | Control Panel - For reading the signals from sensors/detectors, giving audio / visual alarm | ✓
| 2.1 (H) | Other Items (OI) - like Manual Call Points at the entry and exit of various rooms, connecting cables, relays, Audio Visual alarms etc. necessary for commissioning & reliable operation of the AFDAS. | ✓
| 2.3 | The AFDAS shall be self-checking & diagnostic type. It shall continuously monitor the health of the sensors/ detectors & the complete system including battery. The data regarding health & event shall be logged in the system with date & time stamp, which can be downloaded to a PC/ Laptop at later stage. The system should have capacity to store data for up to a minimum of 512 fire events and other events. The Control Panel shall be networkable to the Zonal/Divisional Railway headquarters preferably over TCP/IP and shall have clock synchronization facility. | ✓
| 2.7 | Loop controllers shall have built in interference nullifier so that separate EMI control circuit is not required. The loop distance maybe a minimum of 1.2 Km or as per the recommendation of the manufacturer. | ✓ | ✓
| 2.12 | The AFDAS shall have provision to provide sufficient sets of Programmable Potential Free NO/NC contacts (minimum 3 NO and 3 NC for each room where AFSS is installed), to trigger the Automatic Fire suppression system through logical function as per RDSO/SPN/218/2016 or latest pertaining to Signalling Installations, if provided, switching off the power supply to power equipment /relay room (if required) and for interfacing with the existing Data Logger system. The Current carrying capacity of NO and NC contacts shall be at least 500mA. | ✓
| 2.15.1 | The response time for alarm generation from the time of detection by sensors/detectors shall not exceed ten seconds (NFPA 72 Edition 2016 Para 10.11.1). It shall reliably transmit the detected signal to the Control Panel, so that it can translate this detected signal into suitable alarm signal and warn the railway personal for taking corrective action. | ✓ |  |  |  |  | The requirement in paragraph 10.11.1 of the 2016 edition of NFPA 72 is: "Actuation of alarm notification appliances or emergency voice communications shall occur within 10 seconds after the activation of an initiating device." This section sets the maximum allowable delay for the system to activate the audible and/or visible notification appliances (or initiate emergency voice communications) after a fire or alarm condition has been detected by a device (like a smoke detector, heat detector, or manual pull station).
| 2.15.2 | It shall Indicate or display the location of fire, status of detectors with all stages of alarrms. | ✓
| 2.16 | Power Supply Arrangements for AFDAS: The primary source of supply shall be 110V/230V AC to be given by Railways. In case, failure of primary power supply the system shall work on Secondary power source (battery backup) as part of the system. The minimum cut off voltage for primary shall be specified by OEM. Whenever the primary power supply fails to provide minimum voltage required for operation, the secondary source of power supply shall automatically provide power within 10 seconds (Clause 10.6.6.1 of NFPA 72 Edition 2016). | ✓ |  |  |  |  | "Whenever the primary power supply fails to provide the minimum voltage required for operation, the secondary source of power supply shall automatically provide the power within 10 seconds."
| 2.17 | The System design shall not incorporate use of any radioactive material. A declaration shall be submitted by the supplier in this regard at the time of product approval. |  |  | ✓
| 4.2.1 | 4.2.1.2: The actuating temperature shall be as per the model number offered by the manufacturer. Same shall be considered in type/acceptance test. The manufacturer may specify as many models as possible. The probe type bi-metallic heat detector shall be chosen by the purchaser such that the temperatureterrgerature ratingrating ofof thethe detectedetector shall be at least 11°C above the maximum operating temperature of the diesel generator (Ref: Clause no. 17.6.2.3 of NFPA 72-2016). | ✓ |  |  |  |  | Heat detectors shall be selected so that their assigned temperature classification (see Table 17.6.2.1) is at least 20 degree farenhight (11 degree C) above the maximum expected ambient ceiling temperature in the protected space.
| 4.2.1.3 | It shall be able to detect temperature and shall communicate alarm signal to Control Panel when temperature rises above the defined value. | ✓
| 4.2.2.6 | 4.2.2.6: It shall be UL or FM or Vds or LPCB approved/listed. |  | ✓ |  |  |  | CERTIFICATE TO BE REQUIRED
| 4.3.5 | The detector's alarm condition shall be visible from a distance of 6 Meters (normal condition as per clause 3.1 of IS: 11360) and shall be visually different from the indications of the other conditions. | ✓ | ✓ | ✓ |  |  | ..\..\..\..\..\IS-11360.pdf
| 4.3.8 | The Detector / devices must have inbuilt fault isolator or alternate arrangement at detector level which shall isolate the detector inin case of short circuit or open circuit inthe loop. | ✓
| 4.3.9 | The detectors shall be addressable and resettable type. | ✓
| 4.3.10 | It shall detect the fixed heat above 58°C and the rate of temperature rise (between 6°C/minute to 11.1°C/minute) independently in addition to the photo electric smoke detection. | ✓
| 4.3.12 | Plastic, if used for detector, shall not start softening, deforming, or melting at a temperature lower than 95°C as per Clause 4.2 of IS: 2175-1988. |  |  | ✓ | ✓ |  | ..\..\..\..\..\IS-_-2175.pdf
| 4.3.13 | Smoke detector in this multi-sensor shall be able to detect smoke and shall communicate alarm signal to Control Panel when optical density of smoke/obscuration falls within the limit as follows: % obs/m 1.6 and % obs/feet 0.5 for lower and % obs/m 12.5 and % obs/feet 4.0 for upper. | ✓
| 4.3.14 | The ratio of highest r. t. v. and lowest r. t. v. shall not exceed 1.6 in the least favorable direction, i.e. the direction opposite to the beam of LED. | ✓
| 4.4.1 | The air sampling-type detector system shall be able to withstand dusty environments by onboard monitored air filtering, Auto cleaning facility in optical chamber, electronic discrimination of particle size or other listed methods or combinations thereof. The detector should be capable of providing time delays (< 10 seconds) of alarm outputs to eliminate nuisance alarms due to transient smoke conditions. The detector should also provide facilities for the connection of monitoring equipment for the recording of background smoke level information necessary in setting alert and alarm levels and delays. It shall have event logging facility with date and time stamp. |  |  |  | ✓
| 4.4.2 | Air Sampling Type detector shall use LASER or High-power LED. This type of detector shall use piping or tubing distribution network that shall run from the detector to the areas to be protected. The aspiration fan in the detector housing shall draw air from the protected area and back to the detector through air sampling ports, piping or tubing. At the detector, the air shall be analyzed for fire products. |  |  |  | ✓
| 4.4.3 | The detector shall have the capability of generating four alarm signals depending upon level of smoke detected, for example Example (1): Stage 1-0.5 to 0.95% obs/m Stage 2-1.0 to 1.45% obs/m Stage 3-1.5 to 1.95% obs/m Stage 4 -≥ 2.0% obs/m Example (2): Stage 1-30% of Alarm Stage 4 Stage 2-50% of Alarm Stage 4 Stage 3-70% of Alarm Stage 4 Stage 4-≥ 2.0% obs/m | ✓ |  |  | ✓
| 4.4.4 | The value of the smoke levels may be adjusted depending upon the site conditions. | ✓
| 4.4.5.2 | Maximum transport time from the most remote port to the detection unit of an air sampling system shall not exceed 60 seconds. | ✓ |  |  | ✓
| 4.4.5.3 | Minimum sensitivity settings above ambient airborne levels for the air sampling system installed shall be as follows: Alert condition: 0.2 percent per foot obscuration (effective sensitivity at each port). Alarm condition 1.0 percent per foot obscuration (effective sensitivity at each port). It shall be suitable for operation in a temperature range of 0-49°C. The aspiration type smoke detector should be UL or FM or Vds or LPCB listed/approved. | ✓ | ✓ |  | ✓
| 4.5.1 | The pipes used in the pipe network shall be made of CPVC and shall be listed/approved by UL or FM or Vds or LPCB or tested with appropriate equivalent standard to cater for ceiling temperature of 69°C.The pipe and their assemblies such as couplings, unions, elbows, tees, end caps, capillary tubes, sampling ports, mounting brackets shall be as per the recommendation of manufacturer of Aspirating (Air Sampling) type smoke detector. |  | ✓ | ✓ | ✓ |  | CERTIFICATED TO BE REQUIRED
| 4.5.4 | The system integrator shall carry out the piping design and validate the same with a hydraulic flow calculation generated by using the UL or FM or Vds or LPCB approved software. The appropriate fill density shall be arrived at based on the same. | ✓ | ✓ | ✓ | ✓ |  | CERTIFICATED TO BE REQUIRED
| 4.6.4 | Each core of analogue Linear Heat Sensing cable shall be insulated with a negative temperature coefficient material (Clause 5.1.1.4 of IS: 2189-2008). An outer sheath of high temperature, flame retardant PVC insulation, shall protect the cores. The outer sheath or metallic braid shall not affect the performance of the heat sensor. | ✓ |  |  |  |  | ..\..\..\..\..\IS-_-2189.pdf
| 4.6.8 | The design of the analogue, linear heat sensing cable and corresponding electronic sensing circuits shall be such that the cable length and the number of required loops should be set up to provide optimal coverage for the desired region with cable length ranging from 10m to 200 m. The system shall be designed to have an optimum sensitivity. | ✓
| 4.6.9 | For a given length of sensing cables, it shall be possible to set the alarm temperature at 70°C with an Interface Module and with a tolerance not to exceed ±8.3°C. | ✓
| 4.6.11 | Linear heat sensing cable should be UL or FM or Vds or LPCB approved/listed. |  | ✓ | ✓ |  |  | CERTIFICATED TO BE REQUIRED
| 4.7.1 | LHS Interface should be a microprocessor/microcontroller/PLC based device that communicates between LHS Cable and Control Panel. It should be an intelligent device that will monitor LHS cable for continuity and over temperature fire signatures Performance of the linear heat sensing cable along with its interface module shall be immune to changes in ambient temperature. | ✓ |  |  | ✓
| 4.7.3 | The LHS interface shall be able to distinguish between a Short Circuit Condition & an Actual Fire Event in order to prevent unwanted activation of fire alarm system, in case of an accidental short circuit fault by damage to the sensor or field wiring. | ✓ |  | ✓ | ✓
| 4.7.4 | The LHS interface shall supervise the sensing cable for alarm temperature condition, open & short circuit to generate a fault condition which shall be displayed on the interface module faceplate by the 2 LED indicators: FIRE LED & FAULT LED. | ✓ |  | ✓ | ✓
| 4.7.5 | The LHS interface module shall be suitable for operation in a temperature range of 0- 49°C. |  |  | ✓ | ✓
| 4.7.6 | Linear heat interface module should be UL or FM or Vds or LPCB approved/listed. |  |  | ✓ | ✓ |  | CERTIFICATED TO BE REQUIRED
| 4.8.2 | Linear Heat Detector shall be of temperature sensitive hollow metallic pneumatic tube type. | ✓ |  | ✓
| 4.8.3 | The Linear Heat Detector should have strong capability to withstand the mechanical damage, tensile, water and corrosion and electromagnetic interference. The LHD shall be made of hollow tube of non-corrosive metal/alloy. | ✓ |  | ✓
| 4.8.6 | LHD shall be resettable type. The LHD shall be reusable after detecting the alarm condition. | ✓
| 4.8.7 | The LHD shall provide optimal coverage for the desired region with detector length ranging from 10m to 200 m or more. The system shall be designed to have an optimum sensitivity. | ✓
| 4.8.8 | For a given length of LHD it shall be possible to set the alarm temperature at 70°C with an Interface Module and with a tolerance not to exceed ±8.3°C. | ✓
| 4.8.10 | The LHD interface shall be suitable for operation in a temperature range of 0-49°C. |  | ✓ | ✓ | ✓
| 4.8.11 | Linear heat Detection system (detection tube and its interface module) should be UL or FM or Vds or LPCB approved/listed. |  | ✓ | ✓ | ✓ |  | CERTIFICATED TO BE REQUIRED
| 4.9.1 | Detection, actuation, and control system shall have provision for automatic as well as manual operation. Provision for manual operation shall also be provided in addition to automatic operation. | ✓
| 4.9.2 | The Control Panel shall be the central processing unit of the system, receiving and analyzing signals from Probe type bimetallic heat detectors, UV&IR flame detectors, Heat and Smoke multi sensors, LHS/LHD Interface, Aspirating Type Smoke Detectors and Manual Call Points, for providing audible and visual information to the user. | ✓ |  | ✓ | ✓
| 4.9.3 | It shall have suitable audio-visual alarms for drawing attention/indicating various events. | ✓
| 4.9.4 | It shall also have the capability to electronically/electrically activate and release Fire Extinguishing System, if used any. | ✓
| 4.9.6 | The Control Panel shall have provision to provide sufficient input ports for connecting various sensors/detectors along with their interfaces, if any, & shall have provision to provide sufficient output ports for controlling fire extinguishing system, operating/switching off electrical units and shall have provision for remote monitoring in network. The system shall be approved by UL or FM or Vds or LPCB. The software shall be able to monitor the health of each detector and other devices along with control panel. It shall also have clock synchronization facility | ✓ | ✓ | ✓ | ✓
| 4.9.8 | The control panel shall be designed to work on power supply of 110V/230V AC +10%, - 15% with DC battery backup of adequate capacity. The control panel shall have in-built charging facility for DC battery backup for at least 24 hours for operating the system at quotient load and then 15 minute under fire or emergency condition at maximum connected load (CI. 10.6.7.2.1.2 of NFPA 72 Edition 2016). Addressable modules can be used if required to connect electronics of LHS interface module and Aspiration Typе Smoke Detector to the control panel. | ✓ | ✓ |  |  |  | specifies requirements for the secondary power supply of in-building fire emergency voic. e/alarm communications systems. The code states: An in-building fire emergency voice/alarm communications system is required to have a secondary power supply with sufficient capacity to operate the system under quiescent (non-alarm) load for a minimum of 24 hours. Following the standby period, the system must then be capable of operating all alarm notification appliances at the maximum connected load for an additional 15 minutes.
| 4.9.10 | The front panel of the Control Panel shall have the facility of buzzer silence, alarm silence and alarm activate, lamp test & reset. The front panel shall also indicate the status like fire, fault, disable, test, supply, primary supply fault, secondary supply fault (battery fault) and earth fault by respective LEDs/other suitable means. | ✓
| 4.9.11 | In case of low battery, the system shall give audio visual indication in the control panel. | ✓
| 4.9.12 | The Control Panel shall be able to communicate and display the exact number of the Sensor, which has activated the Fire Detection System, for pinpoint location of the seat of fire. | ✓
| 4.9.13 | It shall be possible to download data and extend alarms from Control Panel through suitable ports like RS485/RS232/USB/TCP/IP into a PC/Laptop at the installation and remote location operating on Windows platform. The software for downloading and analyzing fault data shall be provided & shall be compatible with the latest windows operating system. | ✓
| 4.9.14 | Audio Visual Indication shall be provided on the control panel and get activated in case of fire/smoke, trouble/fault and for supervisory functions. The audio indication may be from piezo électric buzzer and visual indication may be LED indication and/or LCD display. | ✓
| 4.9.16 | The software preferably should have the capability for the following 4 levels of actions: level 1,2,3 and 4 | ✓
| 4.9.17 | The control panel should have provision to connect a GSM module and the system(s) shall send SMSs on GSM network to not less than 5 preselected GSM mobile numbers in case of Level 2, Level 3 and Level 4 signals or as desired by the user. The mobile numbers shall be configurable. SMS shall be generated within 30 seconds of the control panel receiving the detection signals and if the sending fails, subsequent sending of SMS shall be tried by the system immediately. The SIM required for the GSM modem shall be provided by the purchaser. The GSM modem shall be from reputed make and compatible to Quad-band GSM 850, 900, 1800 and 1900 MHz. It shall work on power supply of the AFDAS with suitable power supply adapter. It shall be able to withstand operating temperature 0°C to 49°C and humidity up to 85%. The GSM Module shall be an optional item and shall be supplied as per request of the purchaser. | ✓ |  | ✓ | ✓
| 4.9.18 | The Audio Visual Indication of Control Panel shall have means to indicate the room i.e. Relay Room or Power Equipment Room or DG Room etc., from where the alarm situation has been reported and shall also indicate the location of sensor in that room which has reported the alarm situation. The Control Panel shall activate the fire extinguisher, if used any, of that room only for extinguishing the fire. | ✓
| 4.9.19 | The front panel shall have character display (LED/LCD) and alphanumeric keyboard. | ✓
| 4.9.20 | For Signalling installations at major yards (more than 400 routes and important Junction stations) control panel must have the provisions for working in degrade mode, i.e. during the failure of communication between loop control circuitry and CPU of the control panel shall operate the audio-visual and other output devices in case of an alarm is detected. | ✓
| 4.10.3 | Visual Alarms (Strobe): It shall be preferably flashing type RED/WHITE Color. | ✓
| 4.10.4 | Audio Alarms (Hooter): It shall be preferably with Piezo-electric type sounder. The sound level shall be preferably adjustable type up to 90 dB at a distance of 1m. | ✓
| 4.11.5 | Armored and unarmored shall have anti-rodent outer sheath with Low Smoke Properties. |  | ✓ |  | ✓
| 4.11.6 | Armored & unarmored (CI) cables should meet fire performance test under simultaneous action of Flame, water stress and impacts on single sample at 950°C for minimum 2 hours, certified by LPCB or equivalent. Vendor shall submit certificate for the same. |  | ✓ |  | ✓
| 4.11.10 | The cable manufacturer should provide test certificate related to the manufacturing of fire resistant wires & cables from UL or FM or Vds or LPCB or BRE Global or any recognized lab by Government of India. The vendor shall also give self-certification in this regard. | ✓ | ✓ | ✓ | ✓ |  | certificate to be required
| 4.12.4 | It shall be addressable and resettable. | ✓
| 6.1.1 | The manufacturer must be certified with ISO 9001 (the scope of the ISO Certification has to specifically refer to the manufacturing of the products related to AFDAS). The copy of the certification shall be provided by the manufacturer. The manufacturer in this specification shall at least manufacture the Control Panel, Heat and Smoke Multi Sensor, Audio Visual alarms and Manual Call Pojnt. The manufacturer may outsource the left over items of AFDAS from other firms but shall be responsible for the complete system functioning. The outsourced firms shall be ISO 9001 certified and the certification shall refer to the manufacturing of products being outsourced |  | ✓ |  |  |  | certificate to be required
| 6.1.2 | In case, where OEMs are not listed/approved by UL or FM or Vds or LPCB, the equipment may be listed/approved from any ISO 17065 accredited body which is authorized for carrying out fire detection system certification. |  | ✓ | ✓
| 7.4.1 | Acceptance test shall be carried out on 20% of the lot offered (Minimum 2 of each lot). |  |  |  |  | STAGE INSPECTION REQUIRED OR NOT
| 9 | The test procedure shall be based on the system design. The methodologies to be adopted for various tests shall be decided taking into account the system design/configuration proposed by the manufacturer which shall be approved by RDSO. |  |  |  |  | STAGE INSPECTION REQUIRED OR NOT
| 9.3 | Performance Test | ✓
| 9.4 | The unit shall be functional after applying the rated DC at secondary power source for one minute in the reverse polarity. | ✓
| 9.5 | System Level Tests |  | ✓ |  | ✓
| 9.5.5 | Other Items: |  | ✓ | ✓ | ✓